Load Test Plan

Key Load Testing Methods and Processes

- Short-Circuit Test (Load Loss & Impedance): The secondary winding is short-circuited, and a reduced voltage is applied to the primary side until rated current flows, allowing for the measurement of copper losses and impedance.

Key Aspects of the Short-Circuit Test:

- Setup: The low-voltage (LV) side is typically short-circuited with a heavy conductor, while measuring instruments (ammeter, voltmeter, wattmeter) are connected to the high-voltage (HV) side.

- Procedure: A low-voltage supply is applied to the HV side and gradually increased until the ammeter indicates the rated full-load current flows

- Purpose: This test is essential for determining transformer voltage regulation and efficiency.

EEPower +3

Important Notes:

- Because the applied voltage is very low, the magnetic flux in the core is low, meaning iron losses are neglected.

- It is a non-destructive, economical method for calculating efficiency.

- It is generally performed on the HV side for safer, more precise, and more measurable instrument readings.

_________________________________________________________________________

- Heat Run Test (Temperature Rise): Measures the maximum temperature rise under continuous full-load conditions to ensure the cooling system operates correctly.

Key Aspects of the Heat Run Test:

- Purpose: To verify that the cooling system operates correctly and that the transformer's insulation will not be damaged by overheating.

- Methodology: The transformer is typically tested by applying rated frequency to the primary, with the secondary short-circuited to circulate the rated current.

- Measurements: The test measures the top liquid temperature rise and the average winding temperature rise.

- Duration: The test continues until the temperature stabilizes (i.e., when the temperature rise remains constant over a period).

- Compliance: Results are validated against design specifications and international standards to ensure reliability and performance.

_________________________________________________________________________

- Actual Load Test: The transformer is connected to a load bank (or actual load) at its rated voltage and frequency for 1–2 hours to verify performance parameters like efficiency.

Key Objectives

- Load Loss (Copper Loss) Measurement: Determines losses caused by current in the windings under actual operating conditions.

- Efficiency Evaluation: Calculates efficiency by measuring power input vs. power output.

- Voltage Regulation: Analyzes the change in secondary voltage from no-load to full-load, which is critical for voltage stability.

- Temperature Rise: Assesses the insulation integrity under sustained operational heat.

Kingrun tester +2

Test Procedure

- Preparation: Connect a suitable load bank (resistive or inductive) to the secondary terminals. Ensure all metering instruments (voltmeters, ammeters, wattmeters) are connected to both primary and secondary sides.

- Energize: Apply rated voltage to the primary winding.

- Apply Load: Gradually increase the load on the secondary side until it reaches the rated full-load current.

- Measurements: Record primary voltage, current, and power, as well as secondary voltage and current.

- Data Analysis: Calculate the copper losses, efficiency, and regulation using the recorded data.

Kingrun tester +4

Key Considerations

- Safety: As this involves full power, it requires appropriate precautions to avoid overheating or damage.

- Duration: Often, a heat run test (a type of load test) is conducted for several hours to ensure the temperature rise is within limits.

- Alternative Method: For large transformers, a "short-circuit test" is used to simulate full-load conditions without requiring a full load bank.

_________________________________________________________________________

- Voltage Regulation Test: Measures the change in secondary voltage from no-load to full-load to ensure stability.

Key Details for Testing:

- Definition: Measures the percentage change in output voltage when load changes from zero to rated capacity.

- Formula:

- Test Method: Usually determined via the Short-Circuit Test, where the secondary is shorted, and voltage is applied to the primary until full-load current flows, allowing calculation of equivalent impedance, resistance, and reactance.

- Result Interpretation: Lower regulation percentages indicate better performance (more stable voltage).

- Leading Power Factor: Zero or negative voltage regulation can occur with capacitive loads (leading PF), where the output voltage at full load is higher than at no load.

- Significance: Ensures connected electrical equipment does not receive fluctuating or excessive voltage.

_________________________________________________________________________

Key Parameters Monitored

- Copper Losses: Resistance-based losses at rated current.

- Temperature Rise: Oil and winding temperatures.

- Voltage Regulation: Stability of output voltage.

- Efficiency: Overall operational efficiency.

Standards and Tolerances

- Standards: Tests often comply with IEEE C57.12.00.

- Tolerances: Typically

for two-winding transformers and  for auto-transformers.